## Slide 1: Inertia Forecasting
An emerging topic in the field of energy forecasting
Jemima Graham, Dr Evelyn Heylen, Dr Fei Teng
Inertia Forecasting
03.12.2021

## Slide 2: Outline
Background & Motivation
Current work
  Explanatory model
  Benchmarking
  Spatial-Temporal Considerations
  Feature Development
Future work
Inertia Forecasting
03.12.2021

## Slide 3: Outline
Background & Motivation
Current work
  Explanatory model
  Benchmarking
  Spatial-Temporal Considerations
  Feature Development
Future work
Inertia Forecasting
03.12.2021

## Slide 4: What is power system inertia?
Inertia Forecasting
03.12.2021
Produced by the rotation of generators that are connected synchronously to the grid.
Examples of generators that produce inertia: coal-powered, nuclear, hydropower.
Renewable energy sources do not contribute inertia to the system.
Inertia forecasting: A system operation perspective, Heylen & Teng, 2020; Challenges and opportunities of available inertia estimation methods from a system operation perspective, Heylen et al., Renewable and Sustainable Energy Reviews, 2021
Inertia levels have been decreasing over the last decade.
Notes: Device may fail to correctly operate if frequency not consistent
Device might be damaged

## Slide 5: Why is power system inertia important?
Risk of frequency instabilities due to power imbalances.
System operators have less time to react to imbalances.
Measuring/forecasting the inertia important for decision-making.
Inertia Forecasting
03.12.2021
Inertia forecasting: A system operation perspective, Heylen & Teng, 2020; Challenges and opportunities of available inertia estimation methods from a system operation perspective, Heylen et al., Renewable and Sustainable Energy Reviews, 2021
Image source: Fei Teng, ELEC97102 – Selected Topics in Power Systems, Imperial College London, 2021
Notes: Device may fail to correctly operate if frequency not consistent
Device might be damaged
49.2 max freq deviation for infrequent loss

## Slide 6: Example: Blackout in the UK - 9th August 2019
Lightning strike hit a transmission line.
Cascading failures eventually led to a blackout.
1.1M customers without power for 15 – 50 minutes.
Significant disruption to rail network and critical facilities (Ipswich hospital, Newcastle airport).
Image sources: The Daily Telegraph, BBC news, The Independent
Inertia Forecasting
03.12.2021
Notes: Lightning strike caused a fault on a transmission line
1130 MW of generation lost within one second of fault
Steep decrease in frequency meant that 350- 430MW additional generation tripped off worsening the situation
Frequency response started
But then a gas turbine went offline
Frequency fell to 49 Hz which meant more generators tripped due to protection mechanisms
System freq fell to 48.8Hz at lowest
Managed to get frequency back to 50 Hz within 5 minutes of the fault
All electricity supplies restored through local distribution networks within 45 minutes of the fault

## Slide 7: How is power system inertia managed?
System operator simulates how frequency evolves if largest loss occurs.
24 hours before
  Frequency response services obtained.
24 hours before – real-time
  Additional frequency response procurement (more expensive)
  Deployment of some procured services
  Readjustment of generation mix to limit largest loss.
Inertia Forecasting
03.12.2021
Inertia forecasting: A system operation perspective, Heylen & Teng, 2020

## Slide 8: Unique challenges in inertia forecasting
Limited ground truth data.
    Approximate estimation techniques
    Small data set size
    Some sources of inertia not directly monitored by system operators
  Must be able to deal with decreasing trend (non-stationarities).
Less understanding of the features that contribute to inertia.
Conservative- system operators risk averse.
Inertia Forecasting
03.12.2021
Inertia forecasting: A system operation perspective, Heylen & Teng, 2020; Challenges and opportunities of available inertia estimation methods from a system operation perspective, Heylen et al., Renewable and Sustainable Energy Reviews, 2021
Notes: Limited ground truth data
  Currently approximate inertia estimation techniques are used, e.g.:
    Estimate by generator
    Simple empirical relation
  Small data set size
    Accurate estimates only exist for discrete events
    Near continuous estimate accuracy has not been proven
GE Digital and Reactive Technologies with National Grid ESO
GE Digital have also been working on way to estimate inertia from embedded units

## Slide 9: Existing work in Inertia Forecasting
Inertia Forecasting
03.12.2021
Model | Special Characteristics | Pro | Con | Ref
Time-series forecast | Uses reported online status of generators. | First study into inertia forecasting. | Online status increasingly inaccurate in day-ahead. Does not consider virtual inertia. | Du & Matevosyan
Artificial Neural Network | Forecast regional inertia-like effects (effective inertia). | Does not assume linear or additive relationship. | May lack interpretability. No results published. | Wilson et al.
Du & Matevosyan, Forecast system inertia condition and its impact to integrate more renewables. IEEE Trans. Smart Grid 2018;9(2):1531–3.
D2.3: lessons learned from monitoring & forecasting KPIs on impact of PE penetration. Wilson et al., H2020 MIGRATE project; 2018
Discussed in depth in: Challenges and opportunities of inertia estimation and forecasting in low-inertia power systems, Heylen et al., Renewable and Sustainable Energy Reviews, 2021

## Slide 10: Limitations of existing work
Few existing studies on inertia forecast development.
No existing studies that benchmark the forecast models.
No publicly available data sets calculated by system operators on which to benchmark models.
Inertia Forecasting
03.12.2021

## Slide 11: Outline
Background & Motivation
Current work
  Explanatory model
  Benchmarking
  Spatial-Temporal Considerations
  Feature Development
Future work
Inertia Forecasting
03.12.2021
Unique challenge addressed:
Must be able to deal with decreasing trend (non-stationarities).
Less understanding of the features that contribute to inertia.

## Slide 12: Day-ahead Inertia Forecasting
Model:
  Interpretable
  Robust to non-stationarity of data
  Considers the influence of national demand, wind & solar power, and interconnection flow
Benchmarks: autoregressive model with lag of 48 ( or lag of 48 & 336
+
Inertia Forecasting
03.12.2021
Probabilistic Model for Day-ahead Inertia Forecasting, Heylen et al., IEEE Transactions on Power Systems, 2022

## Slide 13: Explanatory Model for Day-Ahead Inertia Forecasting
where
: day-ahead inertia forecast
: inertia today
: day-ahead national demand forecast
: day-ahead wind power forecast
: day-ahead solar power forecast
: interconnection flow
: time
: coefficient ( denotes whether it is a weekday or weekend/holiday)
Inertia Forecasting
03.12.2021
Probabilistic Model for Day-ahead Inertia Forecasting, Heylen et al., IEEE Transactions on Power Systems, 2022

## Slide 14: Explanatory Forecast Model Development
Image source: Probabilistic Model for Day-ahead Inertia Forecasting, Heylen et al., IEEE Transactions on Power Systems, 2022
Inertia Forecasting
03.12.2021
Notes: Basic model:
Linear correlation analysis to identify demand feature
Then evaluated different models with time, historical inertia, wind forecast, and solar forecast as features (info available in day-ahead) and found this improved accuracy.
Then plotted the residuals against different features not included and found correlation with ic flow which was also included in the model.
Then residuals are also shown to vary depending on whether it is a weekday or weekend/holiday.

## Slide 15: Explanatory Model for Day-Ahead Inertia Forecasting
Publicly available data set (simulated)
Half-hourly forecasts
Training set: 1st January 2016 – 31st December 2017 (Great Britain)
Test set: 1st January 2018 – 31st December 2018 (Great Britain)
Training MAPE: 4.2%
Test MAPE: 4.7%
Outperforms the autoregressive models used as benchmarks
Inertia Forecasting
03.12.2021
Probabilistic Model for Day-ahead Inertia Forecasting, Heylen et al., IEEE Transactions on Power Systems, 2022

## Slide 16: Outline
Background & Motivation
Current work
  Explanatory model
  Benchmarking
  Spatial-Temporal Considerations
  Feature Development
Future work
Inertia Forecasting
03.12.2021

## Slide 17: Aims
Benchmark two forecast models on publicly available data to provide a basis on which objective comparisons can be made
Provide a publicly available Nordic data set for future work in inertia forecasting
Inertia Forecasting
03.12.2021

## Slide 18: Time-Series Model for Short-Term Inertia Forecasting
Preliminary results of time series model to forecast power system inertia.
Forecast for whole of Nordic power system.
Focuses on time series decomposition into a trend component, a seasonality component, and an irregular component.
Inertia Forecasting
03.12.2021
Short-term Kinetic Energy Forecast using a Structural Time Series Model: Study Case of Nordic Power System, Gonzalez-Longatt et al., 2020 International Conference on Smart Systems and Technologies (SST), IEEE, 2020

## Slide 19: Time-Series Model for Short-Term Inertia Forecasting
The system inertia is predicted using the following model:
for
: trend model
  Logistic growth model
: seasonality model
  Fourier series
: irregular component model
  Matrix applied for holidays and special events
Inertia Forecasting
03.12.2021
Short-term Kinetic Energy Forecast using a Structural Time Series Model: Study Case of Nordic Power System, Gonzalez-Longatt et al., 2020 International Conference on Smart Systems and Technologies (SST), IEEE, 2020
Notes: Logistic growth model deals with the non-stationarity of the data
Fourier series – multiple seasonality

## Slide 20: Time-Series Model for Short-Term Inertia Forecasting
The system inertia is predicted using the following model:
for
: trend model | : seasonality model | : irregular component model | : error
Publicly available data set
Minutely forecasts
Training set: 1st January 2018 – 30th January 2018 (Nordic)
Test set: 31st January 2018 (Nordic)
MAPE: 4% (1 hour into the future), 7% (24 hours into the future)
Inertia Forecasting
03.12.2021
Short-term Kinetic Energy Forecast using a Structural Time Series Model: Study Case of Nordic Power System, Gonzalez-Longatt et al., 2020 International Conference on Smart Systems and Technologies (SST), IEEE, 2020

## Slide 21: Nordic Case Study- General Characteristics
Nordic (East Denmark, Finland, Norway, Sweden).
Similar size to Great Britain:
  Peak load: 60 – 70 GW
  Minimum load: 20 – 25 GW
Inertial energy capacity: 390 GWs
Inertial energy in the Nordic decreasing over time.
Multiple seasonalities: annual, monthly, weekly, daily.
Inertial energy in the Nordic between July 2016 and January 2020 decomposed into a trend component, a seasonal component, and a residual component.
Inertia Forecasting
03.12.2021
Future system inertia. Ørum et al. Technical report, ENTSO-E, 2015; Measuring effective area inertia to determine fast-acting frequency response requirements. Wilson et al., International Journal of Electrical Power & Energy Systems, 113:1–8, 2019.

## Slide 22: Nordic Case Study- Hydropower
Generation mix in the Nordic: predominantly hydropower, followed by nuclear and wind.
Generation mix in Great Britain: predominantly natural gas, followed by nuclear and wind.
Inertial energy from hydropower has a decreasing trend.
Inertial energy from hydropower in the Nordic between July 2016 and January 2020 decomposed into a trend component, a seasonal component, and a residual component.
Inertia Forecasting
03.12.2021
Notes: Be careful how you phrase- natural gas contributes inertia too.

## Slide 23: Data set comparison
Nordic (used here)
Publicly available
Calculated by Nordic TSOs
Hourly time resolution
January 2016 – August 2020
Great Britain (used for explanatory model dev)
Publicly available
Simulated
Half-hourly time resolution
January 2016 – December 2018
Inertia Forecasting
03.12.2021
 Nordic data set
Great Britain data set 

## Slide 24: Benchmarking Methodology
Compare the 7% MAPE from the time-series model and the MAPE of the explanatory model on the Nordic data set.
Use the same test set (31st January 2018) for a direct comparison.
Comparison is suitable because there is little variation in inertial energy over the course of an hour.
Inertia Forecasting
03.12.2021

## Slide 25: Benchmarking Results
Model | Training Set | Test Set | Test MAPE (%)
Time-series | 1st January 2018 – 30th January 2018 | 31st January 2018 | 7
Explanatory | 31st January 2017 – 30th January 2018 | 31st January 2018 | 4
Inertia Forecasting
03.12.2021
Explanatory model outperforms time-series model.
Explanatory model generalizable to other energy systems.
Case study | Training MAPE (%) | Test MAPE (%)
Great Britain | 4.2 | 4.7
Nordic | 4.3 | 4.5

## Slide 26: Outline
Background & Motivation
Current work
  Explanatory model
  Benchmarking
  Spatial-Temporal Considerations
  Feature Development
Future work
Inertia Forecasting
03.12.2021

## Slide 27: Temporal Dependency
How is the accuracy of the model affected by the duration of training data?
Using a longer duration of training data found to have a negligible effect.
Best performing model (highlighted) used as base case for spatial granularity investigation and additional feature development.
Training Set Length | Training MAPE (%) | Test MAPE (%)
1 year | 4.539 | 4.420
2 years | 4.320 | 4.505
3 years | 4.197 | 4.862
4 years | 4.426 | 4.553
Inertia Forecasting
03.12.2021

## Slide 28: Introducing Spatial Granularity
Method 1: Forecast inertia in East Denmark, Norway, Finland, and Sweden separately and aggregating results.
Method 2: Use data from individual countries as features instead of data from whole of Nordic.
Method 1 performed well; method 2 performed poorly.
Inertia Forecasting
03.12.2021

## Slide 29: Method 1: forecast countries separately & aggregate.
2.6% (approximately 5000 MVAs) reduction in training MAPE.
3.6% (approximately 7000 MVAs) reduction in test MAPE.
Feature characteristics vary greatly between countries (e.g. Sweden has no solar power).
Does not depend on holidays specific to region.
Inertia Forecasting
03.12.2021

## Slide 30: Outline
Background & Motivation
Current work
  Explanatory model
  Benchmarking
  Spatial-Temporal Considerations
  Feature Development
Future work
Inertia Forecasting
03.12.2021

## Slide 31: Feature Development
Adaptation to Nordic data set.
Introducing monthly interaction variable on the national demand forecast.
Introducing inertia from hydropower feature.
Inertia Forecasting
03.12.2021

## Slide 32: Monthly Interaction Variable
Training Set Length | Training MAPE (%) | Test MAPE (%) | Benchmark Test MAPE (%)
1 year | 3.553 | 7.700 | 4.420
2 years | 3.600 | 3.870 | 4.505
3 years | 3.447 | 4.572 | 4.862
4 years | 3.679 | 4.115 | 4.553
Boxplots of day-ahead national demand forecast grouped by month.
Inertia Forecasting
03.12.2021
The monthly interaction variable improves accuracy but needs at least 2 years worth of data to be well-tuned.
Modelling framework for estimating impacts of climate change on electricity demand at regional level: Case of Greece., Mirasgedis et al., 48(5):1737–1750, may 2007.

## Slide 33: Hydropower Feature
Majority of generation in the Nordic comes from hydropower.
Using hydropower from the previous day as a feature has a negligible impact.
Potential reason: contribution of inertia from hydropower already covered under inertia from the previous day feature.
Inertial energy from hydropower in the Nordic between July 2016 and January 2020 decomposed into a trend component, a seasonal component, and a residual component.
Inertia Forecasting
03.12.2021
Notes: Be careful how you phrase- natural gas contributes inertia too.

## Slide 34: Impact of feature forecast errors
Replace forecasted values with real-time values
Feature forecast errors have a negligible impact (~100 MVAs)
The impact may increase as more renewables are introduced.
Forecast | MAPE/sMAPE (%)
National Demand | 1
Wind Power | 6 (2020), 11-13 (2016-2019)
Solar Power | 1
Inertia Forecasting
03.12.2021
Notes: Impact may increase as more renewables are introduced because if the total uncertainty is low, the system operator will act in a way to reduce the impact on the inertia, but this may not be the case if there are more renewables, and therefore higher uncertainty in the system

## Slide 35: Outline
Background & Motivation
Current work
  Explanatory model
  Benchmarking
  Spatial-Temporal Considerations
  Feature Development
Future work
Inertia Forecasting
03.12.2021

## Slide 36: Unique challenges in inertia forecasting
Limited ground truth data.
    Approximate estimation techniques
    Small data set size
    Some sources of inertia not directly monitored by system operators
  Must be able to deal with decreasing trend (non-stationarities).
Less understanding of the features that contribute to inertia.
Conservative- system operators risk averse.
Inertia Forecasting
03.12.2021
Inertia forecasting: A system operation perspective, Heylen & Teng, 2020; Challenges and opportunities of available inertia estimation methods from a system operation perspective, Heylen et al., Renewable and Sustainable Energy Reviews, 2021
Probabilistic Models
Notes: Limited ground truth data
  Currently approximate inertia estimation techniques are used, e.g.:
    Estimate by generator
    Simple empirical relation
  Small data set size
    Accurate estimates only exist for discrete events
    Near continuous estimate accuracy has not been proven

## Slide 37: Gaussian Parametric Probabilistic Model
Deterministic forecast with a Gaussian error:
  Predicted value is the mean,
  Standard deviation is assumed to be constant and is estimated using the training data.
Improved performance compared to the benchmark autoregressive models.
Used as a benchmark for the non-parametric probabilistic model.
Inertia Forecasting
03.12.2021
Probabilistic Model for Day-ahead Inertia Forecasting, Heylen et al., IEEE Transactions on Power Systems, 2022
Notes: Parametric = defined probability distribution, set # params
Non-parametric = no assumptions about probability distribution

## Slide 38: Non-Parametric Probabilistic Model
Quantile regression: predict a series of quantiles and combine in a piecewise manner.
  Allows skewness of distribution to be considered.
Good calibration in the bulk of the distribution but deviation in the extremities:
  Hybrid model: quantile regression + parametric extremity modelling
  Generalized Pareto Distribution to model extremities (3% upper and lower quantiles).
Inertia Forecasting
03.12.2021
Probabilistic Model for Day-ahead Inertia Forecasting, Heylen et al., IEEE Transactions on Power Systems, 2022
Notes: Calibration = statistical consistency between predicted distribution and the observations
Parametric = defined probability distribution, set # params
Non-parametric = no assumptions about probability distribution
PIT = well calibrated forecasts should have a uniform distribution

## Slide 39: Next steps
Explore how to use the inertia forecasts, especially the probabilistic forecast, in an operational context
Take into account congestion on the transmission lines (using reconciliation forecasting)
Consider privacy-preserving techniques (e.g. federated learning) to encourage sharing of embedded unit data for forecasting
Inertia Forecasting
03.12.2021
Notes: Frequency differs at local level, generation mix in an area driven by demand

## Slide 40: Conclusion
Inertia forecasting is required due to an increased amount of renewable energy sources in power systems.
Work on inertia forecasting is limited, particularly in the area of benchmarking.
The explanatory model outperforms the time-series forecast model on the Nordic case study.
Taking a more spatially granular approach improves results.
Including a monthly interaction variable on the day-ahead national demand forecast improves results.
Inertia Forecasting
03.12.2021

## Slide 41: References
Inertia forecasting: A system operation perspective, Heylen & Teng, 2020
Challenges and opportunities of available inertia estimation methods from a system operation perspective, Heylen et al., Renewable and Sustainable Energy Reviews, 2021
Du & Matevosyan, Forecast system inertia condition and its impact to integrate more renewables. IEEE Trans. Smart Grid 2018;9(2):1531–3.
D2.3: lessons learned from monitoring & forecasting KPIs on impact of PE penetration. Wilson et al., H2020 MIGRATE project; 2018
Probabilistic Model for Day-ahead Inertia Forecasting, Heylen et al., IEEE Transactions on Power Systems, 2022
Short-term Kinetic Energy Forecast using a Structural Time Series Model: Study Case of Nordic Power System, Gonzalez-Longatt et al., 2020 International Conference on Smart Systems and Technologies (SST), IEEE, 2020
Future system inertia. Ørum et al. Technical report, ENTSO-E, 2015
Measuring effective area inertia to determine fast-acting frequency response requirements. Wilson et al., International Journal of Electrical Power & Energy Systems, 113:1–8, 2019.
Modelling framework for estimating impacts of climate change on electricity demand at regional level: Case of Greece., Mirasgedis et al., 48(5):1737–1750, may 2007.
Inertia Forecasting
03.12.2021